## Resistive Input
R | Vin | A/D Counts |  |  | R | Vin | A/D Counts
10 | 0.12195 | 24.9756 |  |  | 1 | 0.012469 | 2.5536
100 | 1 | 204.8 |  |  | 50 | 0.55556 | 113.7778
200 | 1.6667 | 341.3333 |  |  | 100 | 1 | 204.8
300 | 2.1429 | 438.8571 |  |  | 150 | 1.3636 | 279.2727
400 | 2.5 | 512 |  |  | 200 | 1.6667 | 341.3333
500 | 2.7778 | 568.8889 |  |  | 250 | 1.9231 | 393.8462
600 | 3 | 614.4 |  |  | 300 | 2.1429 | 438.8571
700 | 3.1818 | 651.6364 |  |  | 350 | 2.3333 | 477.8667
800 | 3.3333 | 682.6667 |  |  | 400 | 2.5 | 512
900 | 3.4615 | 708.9231 |  |  | 450 | 2.6471 | 542.1176
1000 | 3.5714 | 731.4286 |  |  | 500 | 2.7778 | 568.8889
2000 | 4.1667 | 853.3333
3000 | 4.4118 | 903.5294
4000 | 4.5455 | 930.9091
5000 | 4.6296 | 948.1481 |  | 1K Ohm Pot |  |  |  | 400 Ohm Pot
PV780 Analog input Voltage vs Input Resistance with internal 400 ohm resistor enabled
400 ohm pullup resistor is connected internally to 5Vdc
Formulas
Vin = (5Vdc * Rin)/(400 ohms + Rin)
A/D Counts = Vin/5Vdc * 1024
A/D Counts = (Rin * 1024)/(Rin + 400)

## Temp Sender Example
ES2T Temperature Senders
Temp (C) | Temp (F) | Resistance | A/D Counts
140 | 284 | 40 | 93.0909
130 | 266 | 52 | 117.8053
120 | 248 | 74 | 159.865
110 | 230 | 89 | 186.3722
100 | 212 | 120 | 236.3077
90 | 194 | 164 | 297.7589
80 | 176 | 227 | 370.7305
70 | 158 | 321 | 455.9001
60 | 140 | 460 | 547.7209
50 | 122 | 680 | 644.7407
40 | 104 | 1029 | 737.366
30 | 86 | 1594 | 818.5838
20 | 68 | 2529 | 884.1571
10 | 50 | 4115 | 933.2802
0 | 32 | 7208 | 970.1619

## Pressure Sender Example
ES2P-100 Pressure sending unit
Pressure kPa | Pressure psi | Resistance | A/D Counts
0 | 0 | 240 | 384
69 | 10.0076 | 200 | 341.3333
138 | 20.0152 | 165 | 299.0442
207 | 30.0228 | 135 | 258.3925
276 | 40.0304 | 123 | 240.826
345 | 50.038 | 103 | 209.6859
414 | 60.0456 | 88 | 184.6557
483 | 70.0532 | 74 | 159.865
552 | 80.0608 | 60 | 133.5652
621 | 90.0684 | 47 | 107.6689
689 | 99.931 | 33 | 78.0416

## 4-20mA Input
When 4-20mA is selected the Analog input is shunted to ground through a 200ohm resistor creating a voltage in the range of 0.8V to 4.0V that is fed into the A/D converter
The A/D Converter is 10bits so has a maximum count of 1024 for a 5V input.
Most 4-20mA transmitters have a linear output.
A/D Counts = ((Amps * 200ohms))/5V * 1024 counts
Example PXT-400 Pressure Transmitter
Pressure (psi) | Current (Amps) | A/D Volts | A/D Count
0 | 0.004 | 0.8 | 163.84
100 | 0.008 | 1.6 | 327.68
200 | 0.012 | 2.4 | 491.52
300 | 0.016 | 3.2 | 655.36
400 | 0.02 | 4 | 819.2
Note: When setting up the curve or formula in Powervision don’t forget to allow over and under range measurements so the reading does not go invalid.
The typical pressure transmitter can go up to 24mA output.