## Tables
IX3212 A/D Channels 1 & 2 input Resistance Vs A/D Count
Measurements taken using a decade box with 1% precision resistors with a supply voltage of 12Vdc at room temperature.
NOTE: Bets resolution is at lower resistance values.
Resistance | A/D Count
0 | 0
10 | 4
20 | 9
30 | 13
40 | 17
50 | 22
60 | 26
70 | 30
80 | 35
90 | 39
100 | 43
110 | 48
120 | 52
130 | 56
140 | 60
150 | 64
160 | 68
170 | 72
180 | 76
190 | 80 | The data is linear, approximately a count of 4 per every 10ohms between 0 to 250ohms
200 | 84
210 | 88
220 | 92
230 | 95
240 | 99
250 | 103
300 | 121
400 | 156
500 | 188
600 | 217
700 | 245
800 | 270
900 | 295
1000 | 318
1100 | 339
1200 | 359
1300 | 378
1400 | 396
1500 | 413
1600 | 429
1700 | 445
1800 | 459
1900 | 473
2000 | 486
2100 | 499
2200 | 510
2300 | 522
2400 | 533
2500 | 543
2600 | 553
2700 | 563 | At higher resistance the data becomes non-linear with poorer resolution
2800 | 572
2900 | 581
3000 | 589
3100 | 598
3200 | 605
3300 | 613
3400 | 620
3500 | 627
3600 | 634
3700 | 641
3800 | 647
3900 | 653
4000 | 659
4100 | 665
4200 | 670
4300 | 676
4400 | 681
4500 | 686
4600 | 691
4700 | 696
4800 | 701
4900 | 705
5000 | 710
6000 | 748
7000 | 778 | At highest resistance levels the A/D count only changes about 8 counts/100 ohms diminishing to 5 counts per 1,000 ohms.
8000 | 802
9000 | 822
10000 | 838
11000 | 852
12000 | 864
13000 | 875
14000 | 884
15000 | 892
16000 | 899
17000 | 906
18000 | 912
19000 | 917
20000 | 922

## Calculated values
IX3212 PDM Analog Input 1 & 2 Calculated Values
Resistive Input is pulled high to a 5V reference through a 2.21K resistor.
The A/D converter has a resolution of 0-5Vdc input for a count of 0-1023
The Volatge input to the A/D converter is defined as the ratio of the input resistance to the 2.21K pullup as follows:
Formulas:
Vad = 5V (RI/RI + 2.21K)
A/D Counts = Vad/5v * 1024
Vad = Volatge into the A/D converter
Ri = Input resistance
In Powervision for Color Displays the application returns the value for all analog inputs in Volts DC.
To find resistance when the voltage is known use this formula:
Ri = (1/((5V/Vad)-1) * 2210
Calculating Volts & A/D Count |  |  | Calculating Resistance Input
Ri | A/D Volts | A/D Count | Volts | Ri
10 | 0.022523 | 4.6126 | 0.023 | 10.213
20 | 0.044843 | 9.1839 | 0.045 | 20.0706
30 | 0.066964 | 13.7143 | 0.067 | 30.0162
40 | 0.088889 | 18.2044 | 0.089 | 40.0509
50 | 0.11062 | 22.6549 | 0.111 | 50.1759
60 | 0.13216 | 27.0661 | 0.132 | 59.926
70 | 0.15351 | 31.4386 | 0.154 | 70.2311
80 | 0.17467 | 35.7729 | 0.175 | 80.1554
90 | 0.19565 | 40.0696 | 0.196 | 90.1665
100 | 0.21645 | 44.329 | 0.216 | 99.7826
200 | 0.41494 | 84.9793 | 0.415 | 200.0327
300 | 0.59761 | 122.3904 | 0.598 | 300.2226
400 | 0.76628 | 156.9349 | 0.766 | 399.8252
500 | 0.92251 | 188.9299 | 0.923 | 500.3262
600 | 1.0676 | 218.6477 | 1.068 | 600.2747
700 | 1.2027 | 246.323 | 1.203 | 700.1923
800 | 1.3289 | 272.1595 | 1.329 | 800.079
900 | 1.4469 | 296.3344 | 1.447 | 900.0478
1000 | 1.5576 | 319.0031 | 1.558 | 1000.3428
2000 | 2.3753 | 486.4608 | 2.375 | 1999.5238
3000 | 2.8791 | 589.6353 | 2.879 | 2999.8067
4000 | 3.2206 | 659.5813 | 3.221 | 4001.3547
5000 | 3.4674 | 710.1248 | 3.467 | 4998.0887
10000 | 4.095 | 838.6568 | 4.095 | 9999.9448